
Date 08-10-2014


Dear Venkatesh,
With reference to your RFI, EL-008 please note the following points:

For the varying heights of the ground floors w.r.t electrical layouts 
1. The switch board bottom heights will remain same as given in the legends i.e 1250mm from SSL.
2. The bracket lights height will be  2400mm (as given in the legend) + height difference of the ground floor from the standard ht of 2.9m.
3. The toilet bracket lights will be 2100mm (as given in the legend) + height difference of the ground floor from the standard ht of 2.9m.
4. The AC point will be 2500mm (as given in the legend) + height difference of the ground floor from the standard ht of 2.9m.
5. The geyser socket point will be same as given in the legend i.e 2100mm from SSL.

 Regards
Gauri

