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	Contract Ref: 
	

	
	
	
	Request for Information

	
	
	
	RFI No: EL-11

	Cluster: Elite-1 Typical	Building: E

	To Design Team: 
	Date: 21-10-2014

	Request For Information



	Type of RFI
	Contractual/Commercial
	                  Technical

	Discipline
	Arch.
	Structural
	HVAC
	Electrical
	Plumbing
	Facade
	Others(..........)

	We request clarification of the following:

	Subject: As per pictures attached. 

	1- Pict-01 as attached, SB03 Living Room,  Distance of this module box is 650mm from wall corner, need to shift 100mm i.e. 750mm from wall due to Two S-form panel join, could not fix box on s-form panel (for all typical floors).
2- Pict-02 as attached, SB01 Flat#1 & Flat#6,  150mm from edge of wall, need to be make 100mm.
3- Pict -03 as attached, SB03, Living room lift wall box is 560mm from edge, need 500mm.
Request to clarify the above points. Pictures with marking are attached.


	Signature of Initiator     A.R.Patel 

	Comments from PMO:

	

	

	

	

	

	Signature of PMO

	

	Design Comments      Arch           Structural                   HVAC                      MEP               Facade

	1. For SB03 the distance of the switch board from the wall to be 750mm.
2. SB01 (for flat no. 1 & 6) to be 200mm from the edge of the blockwork wall, since there is a bell switch to be accommodated within the same wall at same height (as that of SB01) on the other side.
3. SB03 in flat no. 3 to be 500mm from the wall.

	
Signed (LODHA Engineer)

	Consultant’s Comments.           KAPL               SJC               StuctBom           WSP                    TCE          Others (........................)

	

	

	

	

	

	

	
Signed (Consultant’s Engineer)
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	Project Director
	Date: -

	
	
	

	
	CC: GM (Commercial)
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